## Sheet1
CFX Project Number:
Site Address:
Inspection Date:
Plan Sheet Number:
Station Number:
# |  | Yes | No | Comments
1 | Electrical service equipment installed per approved plans?
2 | Installed equipment installed per the latest NEC?
3 | Meter installed at proper height (per either Duke Energy or OUC standards)?
4 | Location address permanently riveted onto meter enclosure per power company standards?
5 | Line side disconnect installed at 480V (or higher) locations as per power company standards?
6 | All above ground conduit rigid metal?
7 | Concrete maintenance pad around base of disconnect pole(s)?
8 | Silicone sealant used around top and sides of disconnects?
9 | Silicone sealant used to seal any holes smaller than 1/8" in diameter to limit water intrusion?
10 | Duct sealant used to seal all conduit entry/exit points?
11 | Conduit ground bushings used at the end of all metal conduits?
12 | Neutral ground bond made inside disconnect?
13 | All electrical conductors XHHW or better?
14 | CFX approved surge arrestor installed on load side of wires?
15 | Ground bussbar installed and properly utilized?
16 | Neutral bussbar installed and properly utilized?
17 | 1 wire per terminal lug (includes bussbars) per NEC?
18 | Breaker amperage equal to or higher than safety disconnect or LHUB's breaker amperage?
19 | 40lf of ground rod installed at site inside load side pullbox?
20 | Ground lead properly caldwelded to ground rod (use of split-bolts is not approved)?
21 | OHM reading per CFX standard?
Notes:
Contractor Representative:
CEI Representative:
CFX Representative: